NCTCOG 2024 IMC Safety Essentials — Printable Checklist (Short)

Reminder: These are NCTCOG Recommended Regional Amendments. They only become mandatory if your city adopts them. Always verify local adoption before bidding or building.

0) Adoption check (do this first)

☐ Confirm: Has my city adopted 2024 IMC? Has it adopted the NCTCOG 2024 amendments?

☐ Put a “Codes & Standards Matrix” on the cover sheet (list the adopted editions + dates).

☐ Note in proposal/contract: “Work to the locally adopted code versions.”

1) Attic access (IMC §306.3)

☐ Clear path to remove the largest appliance; opening ≥ 20×30 in.

☐ Passage: height ≥ 30 in, width ≥ 22 in, ≤ 20 ft long (or ≤ 50 ft if the whole path is 6 ft high and 22 in wide).

☐ Continuous floor along the path ≥ 24 in wide.

☐ Level service space in front of unit ≥ 30×30 in.

☐ One of: fixed stair / 300‑lb pull‑down ladder / door from an upper floor.

2) Sloped roof service & fall protection (IMC §306.5.1)

☐ If roof slope ≥ 3:12 and edge > 30 in above grade: provide 16‑in catwalk with cleats ≤ 16 in apart.

☐ Level platform at unit on the service side; platform ≥ 30 in.

☐ Guards around platform: height ≥ 42 in and block a 21‑in sphere (meet IBC loads).

3) Exhaust discharge (IMC §501.3) — use exceptions carefully

☐ Rule: Exhaust to outdoors. Do not exhaust into attics, crawl spaces, or onto walkways.

☐ Local exceptions allowed when conditions are met:

☐ • Whole‑house attic fans into a private attic (dwelling)

☐ • Listed ductless domestic range hoods (and you still meet Chapter 4 ventilation)

☐ • Toilet exhaust may end in a warehouse/shop if outdoor‑air infiltration is present

☐ If using an exception, state the condition in your notes (e.g., dock doors = infiltration).

4) A2L used indoors (high‑probability) (IMC §1104.3.1.1 → ASHRAE 15 §7.6)

☐ Do the room volume / refrigerant charge check (EDVC/RCL).

☐ Use listed refrigerant detection systems/detectors; show model/standard.

☐ Draw the interlocks: leak → fans on / valves closed / alarm.

5) No machinery room path (IMC §1104.2 Exception → ASHRAE 15 §7.4)

☐ Use circuit zoning + automatic safety shut‑off valves (release‑mitigation).

☐ Include valve zoning diagram and control sequence (VRF: branch selector / heat‑recovery boxes).

6) Small A1 charge — shaft exception (IMC §1109.2.5)

☐ Direct system, A1 refrigerant; charge in the smallest occupied room crossed by piping is ≤ Table 1103.1 limit.

☐ Even without a shaft, provide piping protection per §1109.2.2 (sleeves/protective construction).

☐ Attach a one‑page charge vs. room size calc in your submittal.

7) Referenced standards must match your city’s editions (IMC §102.8)

☐ “NFPA 70” means your city’s adopted NEC edition.

☐ If code text conflicts with a product’s listing/installation instructions, follow the listing and instructions (note it on plans).

Where to find details (save these)

NCTCOG Amendments page (adoption status + downloads): https://www.nctcog.org/envir/regional-building-codes/amendments

2024 IMC — NCTCOG Final Recommended Regional Amendments (3 pages): https://www.nctcog.org/getmedia/4a7f3400-4e59-4e0c-8adf-5631a34dc471/2024-IMC-Amendments-Final_Approved.pdf

A2L/IMC Alignment memo (why ASHRAE 15 §§7.4 & 7.6 matter): https://www.nctcog.org/getmedia/e7f32d21-2c7c-4d67-9462-0eedced3c742/2025-Refrigerant-Transition-A2L-and-the-International-Mechanical-Code_01.pdf